变频调速鼓风机停机故障分析及处理

卫国华/中国铝业山西分公司煤气分厂

摘要：简述了煤气鼓风机的运行情况，重点分析了变频器发生故障的原因及处理方法，并提出了加强日常维护的建议。

关键词：离心式鼓风机；变频器；故障诊断

中图分类号：TM344.6    文献标识码：B

文章编号：1006-8155（2008）03-0084-01

Analysis and Treatment for Shutdown Fault of Blowers with Frequency Conversion Adjusting Speed

Abstract: This paper simply describes the operation status of coal-gas blower, and focuses on the analysis of the reason for fault occurred in inverter and its solution. And some suggestions on strengthening runtime maintenance are also pointed out.

Key sords: centrifugal blower; inverter; fault diagnose

0  引言

我厂共有22台TG-3M I型煤气发生炉。生产出的煤气经洗涤塔洗涤、冷却后，进入静电除尘器进一步除尘，净化后的煤气经加压后供生产和生活使用。其中，居民生活用气由一台型号为D110-12（电机功率为30kW）的离心鼓风机加压后送出。2003年，对该风机实施了变频调速改造，由一台JD-BP430变频器控制煤气风机，既保证满足生活用气，又节约电能。

1  故障分析与处理

2007年6月，变频器连续出现几次自动停机故障。图1为煤气风机的主回路原理图。煤气风机首次故障停机时，检查主回路，发现向变频器供电的接触器已断开，变频器失电。从我厂6kV高压配电室了解到，当时电网出现了一次较大的波动，多台没变频调速的风机及水泵也自动停机。因此，判断是由于电网波动造成变频器失电，从而造成风机停机。重启动后，风机运行正常。

几天后，又出现了一次自动停机故障。经查发现接触器闭合，变频器显示低电压保护。当时全厂无一台风机及水泵停机，于是检查变频器低电压保护设定值，发现设定值为85%的额定电压。因为一般的接触器的维持电压在70%额定电压附近，所以初步判定是由于电网波动且波动值在70%～85%额定电压之间，接触器没失电而变频器保护动作。重启动后，风机运行正常（图1）。

不久又出现一次停机，发现变频器仍然显示低电压保护，经了解当时电网非常平稳，于是怀疑是变频器内部故障。接上假负载，采用三相自耦调压器向变频器供电的方式检查。当电压降至95%额定电压时，变频器低电压保护动作，于是确认为变频器内部故障。经对变频器控制回路进行检查，发现测量回路上的一个电压取样电阻（180K）外观发暗，焊下测量，发现其阻值变为20K左右。更换后故障排除。几个月下来，再没出现过自动停机的故障。

2  防范措施

运行期间要对变频器外观及冷却风机等进行认真巡检，变频器运行一段时间后对其控制回路和主回路要进行一次仔细检查，防止出现上述类似问题。只要做到以上两点，就可保证变频器安全稳定运行。

# Text boxes

图1  煤气风机的主回路原理图

————————————

收稿日期：2008-01-22   河津市  043300